WINDMILL PROJECT PROPOSAL

Pasuquin, Ilocos Norte, Philippines

A Feasibility and Siting Study

Submitted in partial fulfillment of course requirements

April 29, 2026

Submitted by:

Dan Mark C. Pastoral

BSME-4A

Pangasinan State University

Submitted to:

Marfel D. Rosario, PME

# I. Executive Summary

This project proposal presents a comprehensive feasibility and siting study for a wind energy farm in Pasuquin, Ilocos Norte. The municipality offers exceptional conditions for wind power generation owing to its position along the Northwest Luzon Wind Corridor, exposure to the Northeast Monsoon (Amihan), and proximity to existing renewable energy infrastructure in the province.

The proposed wind farm aims to harness the abundant kinetic energy of wind along the Pasuquin coastline and ridges, contributing to Ilocos Norte's status as the renewable energy capital of the Philippines. The project will support national energy security goals, reduce reliance on fossil fuels, and stimulate local economic development through job creation and eco-tourism potential.

| Parameter | Details |
| --- | --- |
| Project Location | Pasuquin, Ilocos Norte, Philippines |
| Target Installed Capacity | ~50–100 MW (expandable) |
| Turbine Type | Horizontal Axis Wind Turbine (HAWT) |
| Estimated Turbines | 15–30 units (3–5 MW each) |
| Grid Connection | Luzon Grid via NGCP |
| Project Lifespan | 25–30 years |
| Key Benefit | Clean, renewable baseload power for Ilocos Norte |

# II. Site Selection — Why Pasuquin?

The selection of Pasuquin as the project site is supported by five key factors that make it among the most suitable locations for wind power development in the Philippines.

## 1. High Wind Power Density

Pasuquin is situated along the Northwest Luzon Wind Corridor and is highly exposed to the Northeast Monsoon (Amihan) and prevailing trade winds. Because it sits at a point where wind accelerates as it passes through the Luzon Strait, the area experiences high average wind speeds that are consistent enough to maintain optimal turbine rotation throughout the year.

| Wind Parameter | Value / Description |
| --- | --- |
| Average Wind Speed | ~7–9 m/s (Class 4–5 Wind Resource) |
| Primary Wind Source | Northeast Monsoon (Amihan), Luzon Strait |
| Wind Season | October – March (peak); moderate year-round |
| Capacity Factor (est.) | ~35–45% |

## 2. Strategic Coastal and Hilly Terrain

The municipality features a mix of coastal plains and elevated hilly areas, both of which are ideal for turbine placement:

- Coastal Areas: Coastal Areas provide unobstructed paths for sea winds, allowing turbines to capture consistent wind flows with minimal turbulence.

- Ridge Areas: Ridges allow turbines to capture higher-velocity winds at increased altitudes, maximizing energy output per turbine unit.

## 3. Proximity to Existing Infrastructure

Ilocos Norte is already the hub for renewable energy in the Philippines. With nearby wind projects in Bangui and Burgos, the NGCP transmission grid and logistical routes for transporting heavy turbine components are well-established. This significantly reduces the cost and complexity of connecting a new wind farm to the national power grid.

## 4. Eco-Tourism Potential

Similar to the iconic Bangui Wind Farm, a wind project in Pasuquin can serve a dual purpose — functioning as both a power plant and a tourist landmark. This boosts the local economy by attracting visitors and encouraging the development of small businesses, hotels, and restaurants in the municipality.

## 5. Sustainability and Energy Security

Shifting to wind energy reduces the province's reliance on fossil fuels. Since wind is a free and inexhaustible resource, it provides a hedge against volatile coal and oil prices, leading to more stable long-term energy costs for the region while contributing to national climate change mitigation goals.

# II-B. Process Flow Diagram

The following diagrams illustrate the complete energy conversion process of the proposed Pasuquin Wind Farm — from the kinetic energy of the Amihan winds to the delivery of electricity to the Luzon Grid. Three views are provided: (1) the overall energy flow from wind resource to end users, (2) the physical turbine cross-section with labeled components, and (3) a nacelle cut-away showing the internal mechanical-to-electrical conversion chain.

## A. Wind-to-Grid Energy Flow

The diagram below traces the complete energy pathway through four major stages: Resource (wind assessment), Capture (rotor and nacelle), Conversion (generator and power converter), Transmission (step-up transformer and NGCP grid), and End Use (Ilocos Norte households, industries, and government facilities). Support systems including the SCADA control system and maintenance team are shown as feedback flows.

Figure II-B.1 — Wind-to-Grid Process Flow Diagram (Pasuquin Wind Farm)

## B. Turbine Component Overview

The turbine cross-section below identifies the key physical components of the proposed Horizontal Axis Wind Turbine (HAWT): the rotor blades and hub, the nacelle housing (containing gearbox, generator, and power converter), the tower structure, and the substation connection at the base. Wind from the Amihan enters from the left, driving rotation at the rotor before mechanical energy is converted to electricity within the nacelle and transmitted through the tower to the 33 kV – 115 kV substation.

Figure II-B.2 — Turbine Component Cross-Section with Labeled Parts

## C. Nacelle Cut-Away: Mechanical-to-Electrical Conversion

The nacelle cut-away view details the internal drivetrain of the turbine. The low-speed shaft (rotating at approximately 15–20 RPM) connects the rotor hub to the gearbox. The gearbox steps up the rotation speed at a ratio of approximately 1:90, driving the high-speed shaft at approximately 1,500 RPM. The Doubly Fed Induction Generator (DFIG) converts this rotation into AC electricity. The power converter then stabilizes the frequency to the Philippine grid standard (60 Hz), and the step-up transformer raises the voltage to 33 kV for collection and onward transmission to the substation.

Figure II-B.3 — Nacelle Cut-Away: Low-Speed Shaft to 33 kV Output

# III. Technical Specifications

## A. Turbine Specifications

The proposed project will utilize utility-scale Horizontal Axis Wind Turbines (HAWTs), which are the industry standard for large-scale wind farms. The following specifications are based on commercially available turbine models suitable for the wind resource of Pasuquin.

| Component | Specification |
| --- | --- |
| Turbine Type | 3-Bladed Horizontal Axis Wind Turbine (HAWT) |
| Rated Capacity per Unit | 3.0 – 5.0 MW |
| Rotor Diameter | 120 – 145 meters |
| Hub Height | 90 – 110 meters |
| Cut-in Wind Speed | 3.0 m/s |
| Rated Wind Speed | 12 – 14 m/s |
| Cut-out Wind Speed | 25 m/s |
| Blade Material | Fiberglass-reinforced epoxy composite |
| Generator Type | Doubly Fed Induction Generator (DFIG) |
| Design Lifespan | 25 years (with scheduled maintenance) |

## B. Wind Farm Configuration

The turbines shall be arranged in rows perpendicular to the prevailing Amihan wind direction to minimize wake effect losses. Spacing between turbines shall follow international best practices:

- Turbine spacing (inline): 5–7 rotor diameters (~600–1,000 m)

- Turbine spacing (cross-wind): 3–5 rotor diameters (~360–720 m)

- Minimum setback from residential areas: 500 meters

- Minimum setback from coastline: 200 meters (storm surge buffer)

## C. Electrical and Grid Connection

Each turbine's output will be collected through underground medium-voltage cables to a central substation. The substation will step up voltage for transmission to the Luzon Grid via NGCP interconnection.

| Electrical Component | Details |
| --- | --- |
| Collection Voltage | 33 kV (medium voltage) |
| Substation Step-up | 33 kV / 115 kV transformer |
| Grid Interconnection | 115 kV transmission line to NGCP |
| SCADA System | Real-time monitoring and remote control |
| Power Quality | Compliant with ERC Grid Code Standards |

III. TECHNICAL SPECIFICATIONS

with Design Basis and Engineering Calculations

# A. Turbine Specifications

The selection of turbine specifications is not arbitrary — each parameter is derived from the wind resource characteristics of Pasuquin, IEC standards for wind turbine design, and commercially available technology. This section presents the final specifications alongside the engineering basis for each choice.

## A.1 Rated Capacity per Turbine — Why 3–5 MW?

The rated capacity is determined by the available wind resource and the desired project scale. The calculation below uses the Betz Limit equation to establish the theoretical maximum power extraction from the wind, which sets the upper bound for turbine sizing.

### Step 1 — Wind Power Density Calculation

The kinetic power available in the wind is given by the Wind Power Density (WPD) equation:

P = ½ × ρ × A × V³

Where:

- P = Available wind power (Watts)

- ρ = Air density (kg/m³) — standard at sea level = 1.225 kg/m³

- A = Rotor swept area (m²) = π × r² where r is blade radius

- V = Wind speed (m/s) — using Pasuquin average of 8.5 m/s

### Step 2 — Calculation for a 130-meter Diameter Rotor

| Parameter | Formula / Value | Result | Basis |
| --- | --- | --- | --- |
| Rotor radius (r) | 130 m ÷ 2 | 65 m | Selected rotor diameter |
| Swept area (A) | π × 65² | 13,273 m² | Circle area formula |
| Air density (ρ) | 1.225 kg/m³ | 1.225 kg/m³ | Sea-level standard |
| Wind speed (V) | Pasuquin avg. | 8.5 m/s | Meteorological data |
| Available power (P) | ½ × 1.225 × 13,273 × 8.5³ | ~27.7 MW | Betz equation |
| Betz efficiency limit | P × 0.593 | ~16.4 MW | Betz limit (max 59.3%) |
| Mechanical + elec. losses | ~70% efficiency | ~11.5 MW | Typical drivetrain losses |
| Practical rated output | Conservative margin | 5.0 MW rated | Final turbine rating |

NOTE: The Betz Limit (59.3%) is the theoretical maximum fraction of wind energy that any turbine can extract, derived by Albert Betz in 1919. Real turbines achieve 40–50% of the theoretical maximum due to mechanical and electrical losses.

## A.2 Rotor Diameter — Why 120–145 meters?

The rotor diameter determines how much wind area is swept per rotation. A larger rotor captures more energy but requires stronger structural materials. The optimum diameter is selected to maximize the Annual Energy Production (AEP) relative to turbine cost.

The Specific Power (W/m²) is used as a sizing criterion:

Specific Power = Rated Capacity (W) ÷ Swept Area (m²)

| Rotor Diameter | Swept Area | Rated Capacity | Specific Power | Assessment |
| --- | --- | --- | --- | --- |
| 100 m | 7,854 m² | 3 MW | 382 W/m² | Too high — needs stronger winds |
| 120 m | 11,310 m² | 3.5 MW | 309 W/m² | Acceptable for V = 8 m/s |
| 130 m | 13,273 m² | 4.5 MW | 339 W/m² | Good balance — recommended |
| 145 m | 16,513 m² | 5 MW | 303 W/m² | Best for lower wind sites |

NOTE: Industry benchmark: Specific Power of 250–400 W/m² is optimal for IEC Class II–III wind sites. Pasuquin falls under Class II (7.5–8.5 m/s average), making 130–145 m rotors ideal.

## A.3 Hub Height — Why 90–110 meters?

Hub height is determined by the wind shear profile — wind speed increases with altitude following the Power Law equation:

V(z) = V_ref × (z / z_ref)^α

Where:

- V(z) = Wind speed at desired height z

- V_ref = Reference wind speed at known height (typically 10 m) = 6.5 m/s

- z = Target hub height

- z_ref = Reference height = 10 m

- α = Wind shear exponent = 0.14 (standard for open coastal terrain)

| Hub Height (z) | Calculation | Wind Speed V(z) | % Gain vs. 10 m |
| --- | --- | --- | --- |
| 10 m (ref.) | Base reference | 6.50 m/s | — |
| 50 m | 6.5 × (50/10)^0.14 | 7.58 m/s | +16.6% |
| 80 m | 6.5 × (80/10)^0.14 | 7.98 m/s | +22.8% |
| 90 m | 6.5 × (90/10)^0.14 | 8.10 m/s | +24.6% |
| 100 m | 6.5 × (100/10)^0.14 | 8.19 m/s | +26.0% |
| 110 m | 6.5 × (110/10)^0.14 | 8.28 m/s | +27.4% |
| 150 m | 6.5 × (150/10)^0.14 | 8.57 m/s | +31.8% |

Since wind power is proportional to V³, a 24–27% increase in wind speed at 90–110 m hub height translates to approximately 1.24³ to 1.27³ = 1.91 to 2.05× more power compared to 10 m. This justifies the cost of taller towers. Heights beyond 120 m show diminishing returns relative to structural cost increase.

## A.4 Cut-In, Rated, and Cut-Out Wind Speeds — Basis

The three key wind speeds define the turbine operating envelope and are derived from the site's wind speed frequency distribution (Weibull distribution).

| Speed Parameter | Value | Engineering Basis / Reason |
| --- | --- | --- |
| Cut-in speed | 3.0 m/s | Minimum wind to overcome mechanical friction and produce net positive power. Below this, parasitic losses exceed output. |
| Rated speed | 12–14 m/s | Speed at which turbine reaches full rated output. Corresponds to the peak of the Pasuquin Weibull distribution — maximizes capacity factor. |
| Cut-out speed | 25 m/s | IEC 61400-1 Class II standard. Above this, structural loads on blades and tower exceed safe design limits. Turbine feathers blades and brakes. |

## A.5 Capacity Factor Calculation

The capacity factor is a measure of how much electricity the turbine actually produces compared to its theoretical maximum at full rated power all year.

Capacity Factor (CF) = Actual AEP ÷ (Rated Power × 8,760 hours/year)

| Parameter | Value | Note |
| --- | --- | --- |
| Rated capacity per turbine | 5.0 MW | Selected turbine rating |
| Hours per year | 8,760 hours | 365 days × 24 hours |
| Max theoretical output | 43,800 MWh/year | 5 MW × 8,760 hrs |
| Estimated capacity factor | 38% | Based on Pasuquin wind data (Class II site) |
| Estimated actual AEP | 16,644 MWh/turbine/year | 43,800 × 0.38 |
| Total AEP (20 turbines) | ~332,880 MWh/year | 16,644 × 20 turbines |
| Equivalent households served | ~83,200 households | Avg. 4,000 kWh/yr per household |

NOTE: The 38% capacity factor is a conservative estimate consistent with data from the Bangui (35–42%) and Burgos (36–45%) wind farms in Ilocos Norte, which share similar wind resource characteristics with Pasuquin.

# B. Wind Farm Configuration — Spacing Calculations

Turbine spacing is critical to minimizing wake effect losses. When a turbine extracts energy from the wind, it creates a wake — a zone of reduced wind speed and increased turbulence behind it. If the next turbine is placed within this wake zone, its power output drops significantly.

## B.1 Wake Effect and Spacing Basis

Minimum spacing = N × D

Where D = rotor diameter (130 m) and N = spacing multiplier:

| Spacing Direction | Multiplier (N) | Distance (D = 130 m) | Reason |
| --- | --- | --- | --- |
| Inline (downwind) | 7D | 910 m | Wind recovery distance — wake dissipates after ~7 diameters |
| Cross-wind | 4D | 520 m | Less wake interaction perpendicular to wind direction |
| Min. setback (residences) | N/A | 500 m | Noise limit (IEC: <45 dB at 500 m) and safety |
| Min. setback (coastline) | N/A | 200 m | Storm surge and marine erosion buffer |

## B.2 Land Area Requirement

Based on the spacing above, the estimated land footprint for the wind farm can be calculated:

| Parameter | Calculation | Result |
| --- | --- | --- |
| Turbines per row (cross-wind) | Assumed 4 turbines | 4 units |
| Rows (inline/downwind) | 20 turbines ÷ 4 per row | 5 rows |
| Cross-wind width | 4 × 520 m spacing | ~2,080 m |
| Inline depth | 5 × 910 m spacing | ~4,550 m |
| Total gross area | 2,080 m × 4,550 m | ~9.46 km² |
| Actual turbine footprint | ~400 m² per turbine × 20 | ~0.008 km² (negligible) |
| Land between turbines | Available for agriculture | ~9.45 km² usable |

NOTE: Wind turbines have a very small physical footprint (~20m diameter foundation pad). The land between turbines can continue to be used for farming, grazing, or other compatible land uses — a major advantage over solar farms which require dense panel coverage.

# C. Electrical and Grid Connection — Design Basis

## C.1 Collection Voltage — Why 33 kV?

The collection voltage (voltage at which turbines are connected together underground) is selected based on the total power to be transmitted and the allowable voltage drop.

The key equation for voltage drop in a cable is:

ΔV = (P × R × L) ÷ V²

Where P = power (W), R = cable resistance per km, L = cable length (km), V = voltage (V). Higher voltage dramatically reduces current and therefore losses.

| Collection Voltage | Current at 100 MW | Estimated Line Loss | Verdict |
| --- | --- | --- | --- |
| 11 kV | 5,249 A | ~8–10% | Too high — excessive losses and cable cost |
| 33 kV | 1,750 A | ~1–2% | Industry standard — optimal balance |
| 66 kV | 875 A | ~0.5% | Feasible but over-engineered for this scale |

NOTE: 33 kV is the Philippine and international industry standard for wind farm collection systems up to ~200 MW. This aligns with the existing Bangui and Burgos wind farm infrastructure in Ilocos Norte, simplifying future grid integration.

## C.2 Step-Up Transformer Ratio — 33 kV to 115 kV

The transformer turns ratio is directly derived from the required voltage transformation:

Turns Ratio (N) = V_secondary ÷ V_primary = 115,000 ÷ 33,000 = 3.48 : 1

| Parameter | Value | Basis |
| --- | --- | --- |
| Primary voltage (V_p) | 33 kV | Collection system voltage |
| Secondary voltage (V_s) | 115 kV | NGCP Luzon Grid standard voltage |
| Turns ratio (N) | 3.48 : 1 | V_s ÷ V_p = 115 ÷ 33 |
| Transformer rated capacity | 120 MVA | 20 turbines × 5 MW + 20% contingency |
| Transformer efficiency | ~99.5% | Modern oil-filled power transformer standard |
| Power loss in transformer | ~0.5 MW at full load | 100 MW × 0.5% loss |

## C.3 Why 115 kV for Grid Transmission?

The Philippine grid operates at multiple transmission voltages (69 kV, 115 kV, 230 kV, 500 kV). The selection of 115 kV for Pasuquin is based on:

- Power level: 50–100 MW falls within the 115 kV transmission range (typical: 50–300 MW). Higher voltages are reserved for larger generation plants (>300 MW).

- Existing infrastructure: Ilocos Norte grid: Existing NGCP infrastructure in the province operates at 115 kV, avoiding the need for additional transformation steps.

- Distance: Transmission distance: The Pasuquin–Laoag transmission corridor is approximately 30–40 km, within the optimal range for 115 kV transmission (up to ~100 km).

Summary of Key Design Parameters

| Parameter | Selected Value | Primary Basis |
| --- | --- | --- |
| Rated capacity/turbine | 3–5 MW | Betz limit + Pasuquin V = 8.5 m/s |
| Rotor diameter | 130–145 m | Specific Power = 300–340 W/m² (Class II site) |
| Hub height | 90–110 m | Wind shear: 24–27% speed gain vs. ground level |
| Cut-in speed | 3.0 m/s | Net positive power threshold |
| Rated speed | 12–14 m/s | Pasuquin Weibull distribution peak |
| Cut-out speed | 25 m/s | IEC 61400-1 Class II structural limit |
| Turbine spacing (inline) | 7D = 910 m | Wake recovery distance |
| Turbine spacing (cross-wind) | 4D = 520 m | Minimal wake interaction |
| Capacity factor | 38% | Consistent with Bangui/Burgos actual data |
| Collection voltage | 33 kV | Industry standard, optimal loss vs. cost |
| Transmission voltage | 115 kV | NGCP Ilocos Norte grid standard |
| Transformer ratio | 3.48 : 1 | 115 kV ÷ 33 kV |

# IV. Plant Siting and Layout

## A. Siting Factors

The selection of the specific site within Pasuquin follows the fundamental principles of chemical and industrial plant siting, applied to wind energy:

### 1. Marketing Area

The marketing area for this wind project is the Luzon Grid. Pasuquin is strategically located close to load centers in Ilocos Norte and is connected to the main NGCP transmission backbone. Proximity to the market minimizes transmission losses, analogous to reducing transport costs in conventional industries.

### 2. Raw Materials — Wind Resource

In wind energy, the raw material is the kinetic energy of wind. Unlike conventional fuels, wind cannot be transported; the plant must be located where the resource is abundant. The Pasuquin site offers high average wind velocities from the Luzon Strait, providing the equivalent of a 'cheap and abundant raw material supply' required for viable plant operation.

### 3. Transportation Facilities

Wind turbine components are oversized and heavy-lift cargo, making transportation infrastructure critical. The primary facilities available for the Pasuquin project are:

- Currimao Port — nearest deepwater port for sea freight of nacelles, blades, and tower sections

- Manila North Road (Pan-Philippine Highway) — primary land route for component transport

- Provincial roads will require assessment and reinforcement for wide-load clearance

### 4. Availability of Labor

Two categories of labor are required for the project:

- Skilled: Skilled Technical Workers: Turbine technicians, electrical engineers, and SCADA specialists may be sourced from Ilocos Norte's growing pool of renewable energy professionals trained by existing wind farms in Bangui and Burgos.

- Local: Local Labor: Construction workers, security personnel, and administrative staff from Pasuquin and nearby municipalities will support civil works and long-term operations.

### 5. Water Supply

While wind farms consume significantly less water than thermal power plants, water is still required for blade cleaning (salt removal from sea spray), transformer cooling systems, and administrative facilities. A groundwater assessment of the Pasuquin area is recommended to confirm adequate supply.

## B. Site Layout

The site layout follows the principle of 'process units first,' with ancillary buildings arranged to support efficient operations.

### Process Units — Wind Turbines

Wind turbines are the primary process units and are positioned first based on wind flow analysis. Units shall be placed along the shoreline and ridges of Pasuquin to maximize wind capture. A wake effect analysis using computational fluid dynamics (CFD) modeling will be conducted to optimize turbine placement.

### Ancillary Facilities

| Facility | Purpose | Location Consideration |
| --- | --- | --- |
| Maintenance Workshop & Stores | Storage of spare parts: gears, blades, oil, fasteners | Central to turbine array; accessible by crane vehicles |
| Control Room / SCADA Center | Real-time monitoring of all turbines | Safe distance from main transformer; near substation |
| On-site Substation | Step-up voltage for grid export | Near turbine array centroid; fenced safety perimeter |
| Emergency & Fire Station | Nacelle fire response, high-angle rescue | Accessible to all turbine towers within 5-min response |
| Administrative Building | Project management, visitor reception | Near site entrance; accessible to public |
| Meteorological Mast | Ongoing wind data collection | Exposed location, clear of turbine wake zones |

## C. Safety Distances and Standards

- Turbine-to-turbine spacing: minimum 300–500 m to prevent wake effect

- Setback from residences: minimum 500 m (noise and safety)

- Emergency escape routes: minimum two independent exits from each turbine tower

- Transformers: elevated platforms for flood/storm surge protection and cooling ventilation

- Substation: double-fenced with interlocked safety gates per ERC and IEEE standards

## D. Plant Expansion Provisions

The initial layout shall reserve spare slots in the switchgear and open land areas on Pasuquin ridges for future turbine additions. This ensures that expanding the wind farm does not require dismantling existing infrastructure — a critical consideration for long-term project economics.

# V. Environmental Impact Assessment

## A. Positive Environmental Impacts

| Impact | Description |
| --- | --- |
| GHG Emission Reduction | Each 5 MW turbine avoids ~8,000–10,000 tonnes CO2/year vs coal power |
| Fossil Fuel Displacement | Reduces Ilocos Norte's dependence on diesel and coal generation |
| Air Quality Improvement | Zero direct air pollutant emissions during operation |
| Land Use Efficiency | Turbines occupy small footprints; surrounding land usable for agriculture |
| Marine Ecosystem | No water discharge; no thermal pollution to Luzon Strait waters |

## B. Potential Negative Impacts and Mitigation Measures

| Potential Impact | Mitigation Measure |
| --- | --- |
| Bird and bat mortality | Conduct pre-construction wildlife surveys; install radar-based curtailment systems during migration season |
| Noise pollution | Maintain 500 m setback from residences; use low-noise turbine models; monitor sound levels quarterly |
| Visual impact / landscape change | Community consultation; design turbines consistent with Bangui Wind Farm aesthetic branding |
| Soil erosion during construction | Implement erosion control measures; revegetate disturbed areas post-construction |
| Shadow flicker | Model shadow flicker zones; adjust turbine operating hours if residences are affected |
| Electromagnetic interference | Survey TV/radio signal areas; install signal boosters if needed |

## C. Regulatory Compliance

- Environmental Impact Statement (EIS) required — to be filed with the DENR-EMB

- ECC (Environmental Compliance Certificate) from the Department of Environment and Natural Resources

- DOE Service Contract for Renewable Energy under RA 9513 (Renewable Energy Act of 2008)

- LGU endorsement and Barangay clearances from Pasuquin LGU

- NCIP Free, Prior and Informed Consent (FPIC) if indigenous cultural communities are present in the area

# VI. Financial and Economic Analysis

## A. Project Cost Estimates

The following cost estimates are based on industry benchmarks for wind farm development in the Philippines as of 2024–2025. Actual costs are subject to detailed engineering and procurement studies.

| Cost Item | Estimated Cost (PHP) | Notes |
| --- | --- | --- |
| Wind Turbines (15–30 units) | PHP 3.0 – 6.0 Billion | ~USD 50–60M per 50 MW; FOB cost |
| Civil Works & Foundations | PHP 450 – 900 Million | Road access, tower foundations, grading |
| Electrical & Substation | PHP 300 – 600 Million | MV cables, transformers, SCADA |
| Grid Connection (Transmission) | PHP 200 – 500 Million | NGCP coordination and line extension |
| Project Development & EIS | PHP 50 – 100 Million | Surveys, permits, consultancy |
| Contingency (10%) | PHP 400 – 810 Million | 10% of total CAPEX |
| TOTAL CAPEX (est.) | PHP 4.4 – 8.9 Billion | ~USD 75–155 Million for 50–100 MW |

## B. Revenue Projections

Revenue is generated by selling electricity to the Luzon Grid under a Feed-in Tariff (FiT) or Renewable Portfolio Standard (RPS) mechanism, as administered by the DOE and ERC.

| Revenue Parameter | Estimated Value |
| --- | --- |
| Installed Capacity | 50–100 MW |
| Capacity Factor (est.) | 38% average |
| Annual Energy Output | ~166–332 GWh/year |
| Feed-in Tariff / Selling Price | PHP 8.53/kWh (FiT-2 rate for wind, ERC) |
| Gross Annual Revenue | PHP 1.42 – 2.83 Billion/year |
| O&M Cost (est. 2–3% CAPEX/yr) | PHP 88 – 267 Million/year |
| Simple Payback Period (est.) | 8 – 12 years |

## C. Economic and Social Benefits

- Direct employment: 50–100 permanent jobs during operations (technicians, engineers, security, admin)

- Construction phase employment: 300–500 temporary jobs for local workers

- Local government revenue: Real property tax and business tax contributions to Pasuquin LGU

- Eco-tourism boost: Potential for visitor centers similar to Bangui Wind Farm attraction

- Energy price stabilization: Reduces dependence on imported fossil fuels subject to global price volatility

# VII. Conclusion and Recommendations

The proposed wind farm in Pasuquin, Ilocos Norte presents a compelling case for development based on its exceptional wind resource, strategic location, supporting infrastructure, and alignment with national renewable energy goals. The project is technically feasible, economically viable over a 25-year horizon, and environmentally responsible when proper mitigation measures are applied.

The following next steps are recommended to advance the project:

| Phase | Activity | Timeline |
| --- | --- | --- |
| Phase 1 | Wind resource measurement campaign (met mast installation) | Months 1–12 |
| Phase 2 | Detailed feasibility study and EIS preparation | Months 6–18 |
| Phase 3 | LGU and community consultations; FPIC process | Months 12–24 |
| Phase 4 | DOE Service Contract application and ECC filing | Months 18–30 |
| Phase 5 | Engineering, Procurement & Construction (EPC) | Months 30–48 |
| Phase 6 | Commissioning and grid synchronization | Month 48–54 |

With proper planning, stakeholder engagement, and regulatory compliance, the Pasuquin Wind Farm has the potential to become a landmark renewable energy project in the Philippines — continuing Ilocos Norte's tradition of clean energy leadership while delivering reliable and affordable electricity to the Luzon Grid.

# References

Department of Energy, Philippines. (2023). Renewable Energy Roadmap 2030. Manila: DOE.

Energy Regulatory Commission. (2022). Feed-in Tariff Rates for Renewable Energy Resources. ERC Resolution No. 16, Series 2022.

National Grid Corporation of the Philippines (NGCP). (2024). Grid Development Plan. Quezon City: NGCP.

World Bank Group. (2021). Philippines — Wind Energy Resource Assessment. ESMAP Technical Report.

International Electrotechnical Commission. (2019). IEC 61400-1: Wind Energy Generation Systems — Part 1: Design Requirements. Geneva: IEC.

Philippine Atmospheric, Geophysical and Astronomical Services Administration (PAGASA). Wind Climate Data for Ilocos Norte, 2010–2020.

Republic Act 9513 — Renewable Energy Act of 2008, Republic of the Philippines.

# Section VIII-A — Glossary of Terms and Acronyms

The following technical terms and acronyms appear throughout this proposal. Definitions are aligned with IEC 61400, Philippine DOE, and ERC usage.

| Term / Acronym | Definition |
| --- | --- |
| AEP | Annual Energy Production — total electrical energy generated per year (MWh/yr). |
| Amihan | Northeast Monsoon (Oct–Mar); primary wind driver for Pasuquin. Luzon Strait accelerates these winds. |
| Betz Limit | Theoretical maximum wind energy extractable by any turbine = 59.3% (Albert Betz, 1919). |
| Capacity Factor (CF) | Actual AEP ÷ (Rated Power × 8,760 h/yr). Pasuquin estimate: 38%. |
| CAAP | Civil Aviation Authority of the Philippines — governs aviation obstruction marking on towers. |
| Cut-in Speed | Minimum wind speed for net positive power output. This project: 3.0 m/s. |
| Cut-out Speed | Maximum operating wind speed; above this the rotor feathers. This project: 25 m/s. |
| DENR | Department of Environment and Natural Resources — issues Environmental Compliance Certificate (ECC). |
| DFIG | Doubly Fed Induction Generator — variable-speed generator topology used in this project. |
| DOE | Department of Energy of the Philippines. |
| ECC | Environmental Compliance Certificate issued by DENR-EMB after EIS review. |
| EIS | Environmental Impact Statement — required under the Philippine EIS System (PEISS). |
| EPC | Engineering, Procurement and Construction — main project delivery contract mode. |
| ERC | Energy Regulatory Commission — approves FiT rates, grid codes, and metering standards. |
| FiT | Feed-in Tariff — guaranteed PHP 8.53/kWh for wind energy generators (ERC Res. 16, 2022). |
| FPIC | Free, Prior and Informed Consent — required under RA 8371 (IPRA). |
| HAWT | Horizontal Axis Wind Turbine — 3-bladed upwind configuration; industry standard. |
| Hub Height | Vertical distance from ground to rotor hub center. This project: 90–110 m. |
| IEC 61400 | IEC standard series for wind turbine design, structural loads, and grid integration. |
| MW / MWh | Megawatt (power) / Megawatt-hour (energy). 1 MWh = 1 MW delivered for 1 hour. |
| NGCP | National Grid Corporation of the Philippines — operates the Luzon Grid. |
| NSCP | National Structural Code of the Philippines (2015) — governs tower foundation design. |
| O&M | Operations and Maintenance — ongoing running of the wind farm after commissioning. |
| RA 9513 | Renewable Energy Act of 2008 — legal basis for FiT incentives and DOE service contracts. |
| Rated Speed | Wind speed at which turbine first reaches rated output. This project: 12–14 m/s. |
| SCADA | Supervisory Control and Data Acquisition — remote turbine monitoring and control system. |
| Specific Power | Rated capacity ÷ swept area (W/m²). Optimum for IEC Class II: 250–400 W/m². |
| Swept Area | Circle traced by rotor blades, A = πr². For 130 m rotor: 13,273 m². |
| Wake Effect | Reduced wind speed and increased turbulence behind an operating turbine. |
| Weibull Dist. | Statistical model for wind speed frequency; defined by shape k and scale c. |
| Wind Class II | IEC classification for sites with average wind 7.5–8.5 m/s — Pasuquin's class. |
| Wind Power Density | Available wind power per unit area: WPD = ½ρV³ (W/m²). |
| Wind Shear | Wind speed increase with altitude: V(z)=V_ref·(z/z_ref)^α; α≈0.14 coastal. |

# Section VIII-B — Detailed Equipment Specifications

Specifications are based on the 5.0 MW HAWT, 130 m rotor, 100 m hub height, and 33/115 kV electrical system established in Section III (20-turbine × 5 MW = 100 MW configuration).

## B.1 Rotor and Blade Assembly

| Parameter | Specification | Design Basis |
| --- | --- | --- |
| Configuration | 3-bladed upwind HAWT | Industry standard for utility-scale |
| Rotor diameter | 130 m | Specific Power 339 W/m² — optimal for V=8.5 m/s (Sec. III-A.2) |
| Swept area | 13,273 m² | A = π × (65)² |
| Blade length | 63.5 m | = Rotor radius − hub radius (1.5 m) |
| Blade material | GFRP with carbon-fiber spar caps | IEC 61400-5; fatigue and stiffness |
| Blade weight | ≈ 14,000 kg per blade | Vestas V126/V136 class benchmark |
| Tip speed (max) | ≤ 90 m/s | Acoustic limit and structural fatigue |
| Pitch system | 3 independent electric motors + battery backup | IEC 61400-1 Class II |
| Lightning protection | Receptors at blade tip + down-conductor to ground | IEC 61400-24 |
| Cut-in / Rated / Cut-out | 3.0 / 12–14 / 25 m/s | Sec. III-A.4 Weibull analysis |

## B.2 Drivetrain — Gearbox and DFIG Generator

| Component | Specification |
| --- | --- |
| Gearbox type | Three-stage planetary–helical, integrated with main bearing |
| Gear ratio | 1:90 (rotor ≈17 rpm → generator 1,530 rpm at 60 Hz) |
| Gearbox efficiency | ≥ 97% at rated load |
| Gearbox lubrication | ISO VG 320 mineral/PAO synthetic, 600 L sump, forced |
| Generator type | Doubly Fed Induction Generator (DFIG) — Sec. III-A |
| Rated power | 5.0 MW at 12–14 m/s wind speed |
| Stator voltage | 690 V AC, 3-phase, 60 Hz |
| Generator cooling | Air-to-water heat exchanger inside nacelle |
| Power converter | Partial-scale IGBT (~30% rated) — stabilizes output to 60 Hz |
| Nacelle total mass | ≈ 320 t (nacelle + rotor hub assembly) |
| Overall drivetrain η | ≈ 93% (gearbox × generator × converter combined) |

## B.3 Tower Structure

| Parameter | Specification |
| --- | --- |
| Type | Tubular steel, three-section bolted with flanged joints |
| Hub height selected | 100 m — V(100m) = 8.19 m/s, +26% gain vs. ground (Sec. III-A.3) |
| Base diameter | 4.30 m |
| Top diameter | 3.00 m |
| Wall thickness | 30 mm at base, tapers to 18 mm at top |
| Steel grade | S355 J0+N per EN 10025-2 |
| Tower mass | ≈ 280 t per turbine |
| Coating | ISO 12944 C5-M: zinc primer + epoxy midcoat + PU topcoat, DFT ≥ 320 µm |
| Internal access | Fixed ladder + climb-assist device + emergency descender |
| Aviation marking | Upper 1/3: RAL 3020 red bands per CAAP MOS Part 14 |

## B.4 Electrical Collection System and Substation

| Component | Specification |
| --- | --- |
| Turbine pad-mount transformer | 5.5 MVA, 690 V / 33 kV, oil-filled ONAN cooling |
| Collection voltage | 33 kV — optimal for up to ~200 MW (Sec. III-C.1) |
| Inter-array cable | 33 kV XLPE, copper, 240–630 mm², buried 1.0 m deep, IEC 60502-2 |
| Switchgear per turbine | 33 kV ring-main unit, SF6-insulated |
| Collection feeders | 5 feeders × 4 turbines each ≈ 20 MW per feeder |
| Step-up transformer | 120 MVA, 33 kV / 115 kV, OLTC ±10%, turns ratio 3.48:1 (Sec. III-C.2) |
| Transmission voltage | 115 kV — NGCP Ilocos Norte grid standard (Sec. III-C.3) |
| Substation protection | IEC 61850 relays: 87T diff, 21 distance, 51 overcurrent, 64 REF |
| Reactive compensation | ±30 MVAr STATCOM for Philippine Grid Code compliance |
| Grounding system | Mesh + driven rod earthing, target ≤ 1 Ω resistance (IEEE 80) |
| SCADA system | Wind-Farm Management System, OPC-UA protocol to NGCP RTU |
| Auxiliary power | 500 kVA diesel genset + 30-minute UPS for critical loads |

# Section VIII-C — Plant Layout and 3D Model

This section presents the wind farm site layout and a 3D visualization of the Pasuquin Wind Farm, based on the spacing calculations in Section III-B.2 and the siting factors in Section IV.

## C.1 Plant Site Layout

The layout shows 20 WTGs (WTG-101 to WTG-120) across the Pasuquin coastline and ridges, with the on-site substation, access roads, and ancillary facilities. Turbines: 5 rows × 4 units, 7D (910 m) inline spacing, 4D (520 m) cross-wind spacing per Section III-B.1 wake effect calculations.

[ PLANT LAYOUT — Site plan: turbine positions, substation, access roads, facilities ]

Insert image here — approx. 16 cm × 12 cm

Figure VIII-C.1 — Pasuquin Wind Farm Site Layout Plan

## C.2 3D Model / Rendering

The 3D model illustrates the wind farm along the Pasuquin coastline, showing the scale of turbines (100 m hub height, 130 m rotor) against the terrain, the substation, and the eco-tourism visitor area.

[ 3D MODEL / RENDERING — Perspective view of Pasuquin Wind Farm along the coastline ]

Insert image here — approx. 16 cm × 11 cm

Figure VIII-C.2 — Pasuquin Wind Farm 3D Visualization

Note: Insert finalized layout drawing and 3D rendering above. Recommended: PNG or JPG, minimum 300 DPI, landscape orientation.

# Section VIII-D — Foundation and Anchor Bolt Calculations

Gravity foundation and anchor bolt cage sizing for each turbine tower. Loads: IEC 61400-1 Class II; foundation checked per NSCP 2015.

## D.1 Design Loads at Tower Base

| Load Case | Symbol | Value | Source |
| --- | --- | --- | --- |
| Vertical dead load (rotor + nacelle + tower) | F_z | 4,200 kN | Manufacturer load document |
| Extreme thrust (DLC 1.3 / DLC 6.2) | F_y | 1,050 kN | IEC 61400-1 Class II |
| Overturning moment at tower base | M_y | 115,000 kN·m | F_y × hub height (~100 m) + lever arm |
| Torsional moment | M_z | 8,500 kN·m | Extreme yaw + yaw misalignment |

## D.2 Octagonal Gravity Mat — Sizing

| Parameter | Value | Note |
| --- | --- | --- |
| Outer diameter (across flats) | 21.0 m | Trial size — checked below |
| Slab thickness (edge / center) | 1.0 m / 3.0 m | Tapered frustum for economy |
| Concrete grade | fc' = 35 MPa | ACI 318 / NSCP 2015 |
| Reinforcement | Grade 60 (fy = 414 MPa) | Top + bottom mats, both directions |
| Concrete volume | ≈ 590 m³ | Octagonal frustum formula |
| Foundation self-weight (W_f) | 14,160 kN | γ_c = 24 kN/m³ |
| Soil cover (1.0 m × 380 m²) | 6,840 kN | γ_s = 18 kN/m³ |
| Total stabilizing weight (W_total) | 25,200 kN | F_z + W_f + W_soil |
| Lever arm to edge (e = D/2) | 10.5 m | Half of outer diameter |
| Stabilizing moment (M_s = W_total × e) | 264,600 kN·m | Resisting overturning |
| Safety factor vs. overturning (M_s / M_y) | 2.30 | Required ≥ 1.5 ✓ PASS |
| Max. edge bearing pressure | ≈ 175 kPa | Trapezoidal distribution |
| Required allowable soil bearing capacity | ≥ 250 kPa | Geotech investigation required |

## D.3 Anchor Bolt Cage

| Parameter | Value | Basis |
| --- | --- | --- |
| Total number of bolts | 144 (72 inner + 72 outer ring) | 5 MW class industry standard |
| Bolt grade | ISO 898-1, Class 10.9 (fy ≈ 900 MPa) | High-strength structural |
| Bolt diameter | M48 — effective stress area Aₛ = 1,470 mm² |  |
| Embedded + flange length | 5,500 mm total | Full anchorage depth |
| Pitch circle diameter | Inner 4.20 m / Outer 4.90 m | Matches tower base flange |
| Allowable tension per bolt (Pt) | Aₛ × 0.7 × fy = 925 kN | FoS = 1.5 applied |
| Max. bolt tension (T_max) | M_y × c / I_bolt-group ≈ 605 kN | Linear bolt-group analysis |
| Utilization (T_max / Pt) | 65% | Required ≤ 85% ✓ PASS |
| Pretension torque | ≈ 4,200 N·m via hydraulic tensioner | 70% of fy, per IEC 61400-6 |
| Fatigue check | S-N curve ISO 1099, Class 71 | DLC 1.2 normal operation |

NOTE: All values are preliminary. Final design must be certified by a Philippine-licensed Civil/Structural Engineer based on geotechnical investigation and actual turbine load report.

# Section VIII-E — Facility Inventory and Floor Areas

All facilities on site based on Section IV plant layout. Land between turbines (~9.45 km²) remains usable for farming and grazing.

| No. | Facility | Floor Area (m²) | Function |
| --- | --- | --- | --- |
| 1 | Wind turbine foundations (20 × ~380 m²) | 7,600 * | Octagonal RC mat per Sec. VIII-D |
| 2 | On-site 33/115 kV substation | 5,000 | Step-up transformer, switchgear, control room |
| 3 | SCADA / Control room | 180 | 24/7 supervisory wind-farm control |
| 4 | Maintenance workshop and stores | 650 | Spare parts, gearbox oil, blade tools |
| 5 | Administrative building | 320 | Project management, visitor reception |
| 6 | Eco-tourism visitor center | 400 | Public viewing deck, exhibits, restrooms |
| 7 | Emergency and fire station | 240 | Nacelle fire response, high-angle rescue |
| 8 | Diesel genset house + fuel storage | 120 | 500 kVA backup + 5,000 L diesel tank |
| 9 | Meteorological mast pad | 100 | Permanent met mast and instrumentation |
| 10 | Guard house and main gate | 60 | 24/7 security checkpoint |
| 11 | Parking and crane turnaround | 1,200 | Heavy vehicles, mobile crane hardstand |
| 12 | Material laydown / crane hardstand | 2,500 | Blade/nacelle staging (construction) |
| 13 | Septic and sewage treatment | 150 | On-site sanitary waste treatment |
| 14 | Water tank and pump house | 80 | Blade wash, fire-reserve tank (50,000 L) |
| 15 | Internal access roads (7 km × 6 m wide) | ≈ 42,000 | Heavy-haul gravel roads to each WTG |
|  | TOTAL BUILT-UP FACILITIES (excl. roads + turbine pads) | ≈ 11,000 |  |
|  | TOTAL TURBINE FOUNDATION FOOTPRINT (*) | ≈ 7,600 |  |
|  | TOTAL ROADS AND HARDSTANDS | ≈ 44,500 |  |
|  | GROSS WIND FARM AREA (including inter-turbine land) | ≈ 9.46 km² | Per Sec. III-B.2 |

# Section VIII-F — Energy Balance Diagram

Extends the Process Flow Diagrams in Section II-B by quantifying power losses at each stage — from wind kinetic energy to electricity at the NGCP grid metering point.

## F.1 Stage-by-Stage Power Balance (per turbine at V = 12 m/s)

Basis: P_wind = ½ × ρ × A × V³ = ½ × 1.225 × 13,273 × 12³ = 13.96 MW (same Betz equation as Section III-A.1).

| Stage | Input (MW) | Loss (MW) | Output (MW) | Loss Mechanism |
| --- | --- | --- | --- | --- |
| Wind kinetic energy at rotor disc | 13.96 | — | 13.96 | P_wind = ½ρAV³ |
| Aerodynamic conversion (Cp = 0.45) | 13.96 | 7.68 | 6.28 | Real rotor < Betz 59.3% |
| Hub + main bearing friction | 6.28 | 0.06 | 6.22 | ≈ 1% mechanical losses |
| Gearbox (3-stage planetary, η = 97%) | 6.22 | 0.19 | 6.03 | ≈ 3% gear losses |
| DFIG generator (η = 97%) | 6.03 | 0.18 | 5.85 | ≈ 3% electromagnetic losses |
| Partial-scale power converter | 5.85 | 0.10 | 5.75 | ≈ 1.7% IGBT losses |
| Pad-mount transformer 690 V / 33 kV | 5.75 | 0.05 | 5.70 | ≈ 0.9% iron + copper losses |
| Inter-array 33 kV cable (average) | 5.70 | 0.04 | 5.66 | ≈ 0.7% I²R losses |
| Step-up transformer 33 kV / 115 kV | 5.66 | 0.03 | 5.63 | ≈ 0.5% transformer losses |
| 115 kV OHL to Laoag (≈ 35 km) | 5.63 | 0.05 | 5.58 | ≈ 0.9% line losses |
| NET at NGCP grid metering point | — | — | 5.58 | Useful electricity delivered |

## F.2 Annual Energy Yield — Wind Farm Total

| Parameter | Value | Calculation / Basis |
| --- | --- | --- |
| Rated capacity per turbine | 5.0 MW | Design specification (Sec. III-A.1) |
| Max theoretical AEP per turbine | 43,800 MWh/yr | 5.0 MW × 8,760 h/yr |
| Capacity factor — Pasuquin | 38% | Consistent with Bangui 35–42%, Burgos 36–45% |
| Gross AEP per turbine | 16,644 MWh/yr | 43,800 × 0.38 |
| Electrical system losses (avg. 7%) | 1,165 MWh/yr | Cables, transformers, line |
| Net AEP per turbine delivered | 15,479 MWh/yr | 16,644 × (1 − 0.07) |
| Wind farm total (20 turbines) | 309,580 MWh/yr | 15,479 × 20 turbines |
| Equivalent households served | ≈ 77,400 | At 4,000 kWh/yr per household (PH avg.) |
| Annual FiT revenue (gross) | PHP 2.64 Billion/yr | 309,580 MWh × PHP 8.53/kWh |

# Section VIII-G — Operations and Maintenance (O&M) Plan

Sustains the 38% capacity factor assumed in the financial analysis (Section VI) across the 25-year project life.

## G.1 Permanent Staffing

| Role | No. | Shift Schedule |
| --- | --- | --- |
| Wind Farm Manager | 1 | Day |
| Lead Turbine Technician (GWO Level 3) | 4 | Day + on-call rotation |
| Turbine Technician (GWO Level 2) | 8 | Day, 4-on/4-off rotation |
| Electrical / Substation Engineer | 2 | Day |
| SCADA Operator | 4 | 24/7, four-shift rotation |
| HSE Officer / GWO Safety Trainer | 1 | Day |
| Admin and Procurement Staff | 2 | Day |
| Security Personnel | 6 | 24/7 |
| TOTAL | 28 |  |

## G.2 Preventive Maintenance Schedule (per turbine)

| Frequency | Activity |
| --- | --- |
| Continuous (24/7) | SCADA monitoring: vibration, temperature, power output, fault alarms |
| Weekly | Ground-level visual + drone oil-leak inspection |
| Monthly | Tower climb: bolt torque check, lubrication top-up, brake pad inspection |
| Quarterly | Gearbox oil spectroscopy; blade leading-edge visual check |
| Semi-annual | Yaw and pitch function test; emergency descender re-certification |
| Annual | Full PM: oil change, filter change, bolt re-torque (all 144 anchor bolts) |
| Every 2 years | Generator slip-ring service; Philippine Grid Code compliance test |
| Every 5 years | Major: gearbox borescope, blade UT scan, transformer oil DGA |
| Every 10 years | Mid-life overhaul: gearbox refurbishment, generator rewind assessment |

## G.3 Spare Parts Strategy (Tiered Inventory)

- Tier A — On-site (immediate): pitch/yaw motors, fuses, contactors, sensors, lubricants, filters.

- Tier B — Regional depot, 24 h delivery: IGBT converter modules, slip rings, brake pads, hydraulic accumulators.

- Tier C — Manufacturer warehouse, 2–6 weeks: main bearing, gearbox sub-assembly, generator, blade section.

## G.4 Safety and Compliance

- All technicians must hold valid GWO BST certificate: Working at Heights, First Aid, Manual Handling, Fire Awareness.

- Two-person rule enforced for any work above 30 m inside or outside the tower.

- Hot-work permits required for welding or grinding inside the nacelle.

- Annual emergency drill: nacelle fire, tower rescue, medical evacuation.

- All work compliant with DOLE Department Order No. 198-18 (OSH Standards).

# Section VIII-H — Materials and Color-Coding Standards

## H.1 Material Specifications

| Component | Material / Grade / Standard |
| --- | --- |
| Tower steel | S355 J0+N per EN 10025-2 |
| Tower flange bolts | ISO 898-1 Class 10.9, hot-dip galvanized |
| Anchor bolts | ISO 898-1 Class 10.9 or ASTM A615 Grade 75 |
| Foundation concrete | fc' = 35 MPa; ACI 318 / NSCP 2015 |
| Foundation rebar | Grade 60 (fy = 414 MPa) deformed bars — top + bottom mats |
| External coating | ISO 12944 C5-M: zinc primer + epoxy + PU topcoat, total DFT ≥ 320 µm |
| Blade composite | Glass-fiber reinforced epoxy (GFRP) + carbon spar caps; IEC 61400-5 |
| 33 kV inter-array cable | XLPE-insulated, copper, Class 2; IEC 60502-2 |
| 115 kV overhead conductor | ACSR 'Drake' per ANSI/NEMA; NESC clearances |
| Substation grounding | Bare copper 95 mm² mesh; IEEE 80 — target ≤ 1 Ω |
| Control cabinets | IP66 painted steel; RAL 7035 light grey |
| Gearbox lubricant | ISO VG 320 mineral or PAO synthetic |
| Yaw/pitch grease | NLGI-2 lithium-complex with EP additive |

## H.2 Color-Coding Scheme

| Item | Color (RAL) | Standard / Reason |
| --- | --- | --- |
| Tower body — lower 2/3 | RAL 9010 Pure White | IEC / aviation standard |
| Tower body — upper 1/3 (2 red bands) | RAL 3020 Traffic Red | CAAP MOS Part 14 — daytime obstruction |
| Blade tips (last 6 m, alternating) | RAL 3020 + RAL 9010 | Aviation visibility |
| Aviation warning lights | Red, medium-intensity flashing | ICAO Annex 14 / CAAP |
| Earthing / grounding conductors | Green/Yellow striped | IEC 60446 |
| 33 kV cable phase marking | L1=Red, L2=Yellow, L3=Blue | PEC 2017 Philippine standard |
| Fire-fighting equipment | RAL 3000 Flame Red | DOLE OSH standards |
| Emergency exits and routes | RAL 6024 Traffic Green + white text | ISO 7010 |
| 115 kV substation control panels | RAL 7032 Pebble Grey | Philippine substation convention |
| Hazard / caution floor markings | RAL 1023 Traffic Yellow + black stripes | ISO 3864 |
| Transformer oil containment bund | RAL 1018 Zinc Yellow | High visibility for inspection |